Updating Interconnection Screens for PV System Integration

Michael Coddington, Benjamin Kroposki, Barry Mather – NREL Kevin Lynn, Alvin Razon – DOE Abraham Ellis, Roger Hill – SNL Tom Key, Kristen Nicole, Jeff Smith - EPRI

Contents

1	Overview and Purpose	1

2	Interconnection Procedures	1

3	The 15% Threshold	2

3.1	Unintentional Islanding	3

3.2	Voltage Control	4

3.3	Protection Coordination	5

4	Upgrading the 15% Screen	5

5	Short-Term Solutions	6

5.1	Base Screen on Minimum Daytime Load	6

5.2	Apply Supplementary Screens	9

5.3	Utility Identified Zones of Penetration Levels	12

6	Mid-Term and Long-Term Solutions	13

6.1	Upgrade Distribution Circuit Design for PV-Hosting Applications	13

6.2	Develop Higher Accuracy Screening Metrics and Formulas	14

6.3	Deploy Inverters with Advanced Functions	14

7	Conclusions and Next Steps	17

# Overview and Purpose

Solar photovoltaics (PV) is the dominant type of distributed generation (DG) technology interconnected to electric distribution systems in the United States and deployment of PV systems continues to increase rapidly. In states such as California, Hawaii, and New Jersey alone, the number of new PV interconnection applications is in the thousands each year. Considering the rapid growth and widespread deployment of PV systems embedded in United States electric distribution grids, it is important that interconnection procedures be as streamlined as possible to avoid unnecessary interconnection studies, costs, and delays.

Since many PV interconnection applications involve high penetration scenarios, the process needs to allow for a sufficiently rigorous technical evaluation to identify and address possible system impacts. Existing interconnection procedures are designed to balance the need for efficiency and technical rigor for all DG. However, there is an implicit expectation that those procedures will be updated over time in order to remain relevant with respect to evolving standards, technology, and practical experience. Modifications to interconnection screens and procedures must focus on maintaining or improving safety and reliability, as well as reducing costs and improving expediency of the interconnection process.

The purpose of this paper is to evaluate the origins and usefulness of the capacity penetration screen, offer short-term solutions which could effectively allow fast-track interconnection to many PV system applications, and considers longer-term solutions for increasing PV deployment levels in a safe and reliable manner while reducing or eliminating the emphasis on the penetration screen. Short-term and longer-term alternatives approaches are offered as examples; however, specific modifications to screening procedures must be discussed in the context of established stakeholder and regulatory processes.

# Interconnection Procedures

Interconnection procedures vary depending on state or federal jurisdiction. In May 2005, the Federal Energy Regulatory Commission (FERC) adopted small generator interconnection procedures for distributed energy resources up to 20 megawatts in capacity. The Small Generator Interconnection Procedures (SGIP) apply to facilities that fall under federal jurisdiction, those that participate in wholesale market transactions, whether they connect at the transmission or distribution level. Interconnection at the distribution level is mostly regulated by state public utilities commissions; however, state-specific procedures are closely modeled after FERC’s SGIP.

Most procedures allow for expedited interconnection without additional technical studies if the proposed interconnection passes a series of technical screens. If a proposed interconnection fails one or more of the screens, supplemental interconnection studies may be required before it can proceed to interconnection. These additional studies can have a significant impact on the time and cost it will take to process the interconnection request.

# The 15% Threshold

In 1999, before the FERC SGIP was established, the California Public Utilities Commission (CPUC) issued an order instituting a rulemaking to address interconnection standards for devices to the electric grid in California. The order resulted in CPUC Rule 21. During the development of CPUC Rule 21, a 15% threshold was established to identify situations where the amount of DG capacity on a line section exceeds 15% of the line section annual peak load. The 15% threshold was adopted by the FERC SGIP is used by most states as a model for developing their interconnection procedures. Under most applicable interconnection screening procedures, penetration levels higher than 15% of peak load trigger the need for supplemental studies.

The 15% threshold is based on a rationale that unintentional islanding, voltage aberrations, protection miscoordination, and other potentially negative impacts are effectively eliminated if DG generation is always less than the minimum load.

There are three different measures to describe penetration levels: instantaneous, energy, and capacity. Instantaneous penetration is defined as the output power of total DG on a circuit divided by the circuit load at any particular instance in time. This value will change over time depending on the load conditions and power output from DG. Energy penetration is the ratio of energy generated on a circuit divided by energy consumed by load over a specific period of time (typically one year). Capacity penetration is defined as the output power of the total DG on a circuit divided by the peak annual load on that circuit. The capacity penetration threshold is expressed in terms of peak load, as opposed to the intended metric (minimum load) because peak load data is tracked and accessible to utilities.

Figure 1 summarizes the FERC SGIP initial review process, from which many states have adopted the same or a similar set of screens. The first screen examines total penetration by capacity, defined as the ratio of total DG capacity to the annual peak load, and determines whether penetration level is less than 15% of the line-section annual peak load. This 15% threshold applies to radial distribution circuits (a circuit with only one supply point), which is the most common type of distribution circuit with interconnected PV systems. . For typical distribution circuits in the United States, minimum annual load is approximately 30% of annual peak load. The actual ratio varies widely depending on many factors such as the type of load served. Based on this generalization, the 15% penetration level (one half of the 30%) was selected as a conservative penetration level for general screening purposes.

Figure 1 – FERC SGIP initial review screens summarized

Originally, the purpose of the 15% screen was to identify situations where the amount of DG penetration may be large enough to sustain an unintentional island, a condition deemed hazardous to utility personnel and possibly damaging to loads. The threshold was also intended as a “catch all” rule to eliminate other possible problems related to voltage control and system protection. There considerable debate on whether more efficient and appropriate screening criteria can be used, especially in light of the fact that that this screen, more than any other, triggers the need for additional studies. In addition, PV systems have unique technical characteristics that, if taken into account, could lead to a more efficient and effective screening procedure. The following sections discuss these technical issues from the point of view of PV and how it relates to the 15% screen.

## Unintentional Islanding

Risks from unintentional islanding conditions include unacceptable voltage and frequency levels, transient over-voltage conditions, equipment damage, and safety effects. Grid-connected PV inverters have anti-islanding features built into the controls, and are required to be “certified” for the intended use, meaning that they must have UL 1741 certification and meet IEEE 1547 grid compatibility requirements. The possibility of PV inverters unintentionally islanding is very low because UL 1741-listed inverters use anti-islanding algorithms that allow them to drop off line within two seconds after an island is formed.

Unintended islanding is a particular concern when PV and legacy synchronous DGs, such as diesel generators, are connected to the same line section. If the legacy generators do not properly detect the island condition, they may mimic normal grid conditions, causing the PV inverters to stay online.

A significant utility concern is that the unintentional islanding test in UL 1741 is conducted on only one inverter at a time. For this reason, some argue that multiple inverters could interfere with each other in such a way as to increase the chances that an unintentional island will occur. While it is not possible to reduce the risk to zero, the reality is that the risk is extremely low, considering all the factors that need to be concurrently present. The most compelling evidence is that incidents of unintentional islanding are extremely rate in actual field experience despite numerous examples of high penetration scenarios that exist. There are only a couple of documented exceptions, and all are related to special circumstances such as presence of non UL-listed equipment. While a complete discussion of anti-islanding techniques is outside the scope of this paper, there are some simple concepts that can be incorporated in screening procedures to assess the risk of unintentional islanding.

## Voltage Control

The greatest concern and most commonly reported problem associated with high penetration in distribution feeders is high steady-state voltage. When power is injected into a part of the electric power system that normally serves load the voltage at that location tends to increase. With higher penetration, higher voltages are expected along a feeder. The voltage effect depends on the feeder characteristics (voltage rating, conductor size, conductor material, overhead or underground) and location of PV along the feeder. Because feeders are designed to be larger, thus “stiffer”, near the substation, and because voltage control equipment is electrically closer, the impact from PV is lessened as the distance to the substation is lessened. Conversely, as PV systems are located longer distances from the substation the stiffness decreases and the potential for high voltages becomes greater (especially during periods of light load such as weekend days).

Figure 2 illustrates the possible impact of PV on steady-state voltage. On a circuit with no DG present, the voltage along the feeder decreases as distance from the substation increases. If PV power injected into the circuit is high enough, the voltage will increase, potentially taking the voltage above normal operational conditions (5% above nominal). PV located close to the substation can also affect steady-state voltage regulation by “masking” part of the load and thus interfering with load-controlled voltage regulation equipment.  In either case, the net result is that high penetration would make it more challenging to maintain acceptable voltage regulation.  It should be kept in mind that 15% penetration threshold, by itself, is not a good indicator of when steady-state high voltage are likely to occur.  For the vast majority of the cases, voltage control issues are not of concern until penetration levels are much higher than 15%.

Figure 2 – Example of voltage rise problem for a high penetration scenario

Similar to high voltage issues, if the PV system is located further from the distribution substation, PV output variability can result in significant voltage variability. Possible consequences are poor voltage regulation and increased cycling and stress on voltage control equipment (line regulators and switched capacitor banks) leading to more frequent and costly maintenance. Again, the 15% penetration threshold, by itself, is not a good indicator of when these types of impacts are likely to occur. Based on field experience, these issues are associated with penetration levels much higher than 15% penetration.

## Protection Coordination

Unlike rotating machines, a PV inverter’s contribution to fault current is limited and not likely to cause protection problems; however, screening procedures routinely check for coordination and grounding compatibility.  In some PV inverter installations an effectively grounded neutral is required in order to reduce the potential for temporary overvoltage during unbalanced system faults. Multiple ground sources can increase ground current contribution and affect the sensitivity of ground current protection functions at the substation.

# Upgrading the 15% Screen

During review of PV interconnection requests, the 15% interconnection screen most often triggers the need for supplemental studies. In most cases, even when PV penetration is substantially above 15%, the supplemental review does not identify any necessary system upgrades. It is well known that there are many circuits across the United States with PV penetration levels well above 15% where system performance, safety, and reliability have not been materially affected.

These observations indicate that the existing 15% screen is conservative most of the time and is not an accurate way of determining the hosting capability (ability to add more PV without system upgrades) of a particular feeder. The following short-term, mid-term, and long-term approaches are recommended to improve screening procedures for distribution-connected PV systems and other DG resources.

# Short-Term Solutions

Inverter-based PV has unique technical characteristics that minimize the impacts on grid operations. Unlike other DG resources, the output pattern of PV is strictly diurnal (active in daytime). The grid-PV interface is an electronic inverter with adjustable settings and short circuit current much lower than synchronous generators of the same output rating. PV inverters are designed to comply with IEEE 1547 standards and UL-1741 certification without the need for external protection or controls. By taking into account these technical characteristics, it is possible to refine screening procedures to be more efficient and effective, substantially reducing interconnection process time and effort for PV deployment without compromising safety and reliability of the interconnected distribution system. Several possible approaches could be undertaken in the short term to improve screening procedures for distribution-connected PV systems.

There are three conceptual examples discussed in this section. The first approach is to include a PV-specific screening criterion that utilizes the minimum daytime load instead of the absolute minimum load.  The second approach is to apply additional screens to identify possible technical issues, regardless of penetration level. Finally, the third approach is to increase the penetration levels by identifying zones of higher penetration based on the utility distribution feeder configuration and location of substations.

## Base Screen on Minimum Daytime Load

The fact that PV generation has a strictly daytime pattern is significant considering that voltage impacts tend to be greater during periods of highest instantaneous penetration. By the time PV systems are producing a substantial amount of power, loads are well above their nightly lows on most feeders. Therefore, it makes sense to consider minimum daytime load as a technical screening criterion. For example, a screen may set a threshold at minimum daytime load, where daytime is defined as the period between 10:00 a.m. and 2:00 p.m. A simple modification of the SGIP screening criteria to implement this PV-specific screening criterion is depicted in Figure 3. If the PV system passes the additional screen it passes the penetration screen.

Figure 3 – Modified SGIP screens to address PV interconnection based on minimum daytime load

If actual historical data is available, load data in areas of interest could be analyzed to establish factors that relate minimum daytime load levels to peak load levels. Some utilities already use minimum daytime load as a screening criterion and have determined these load levels for their service territory. Figure 4 illustrates a typical circuit where the annual minimum daytime load is much higher than the minimum annual load (24-hour minimum). Figure 5 shows the comparative ratios of minimum load and minimum daytime load (to peak load) for 500 residential and commercial feeders, and shows what percentage of the feeders analyzed have minimum to peak load ratio below 0.2, 0.3, 0.4, and 0.5 based on minimum 24-hour load as compared to minimum daytime load.  For example, the figure shows that 45% of feeders analyzed have ratios below 0.3 based on 24-hour minimum load, whereas only 20% of the feeders have ratios below 0.3 based on minimum daytime load.

It may be difficult to establish minimum daytime unless reliable historical data is available; however, many utilities have access to minimum and peak load data via Supervisory Control and Data Acquisition (SCADA) systems. If SCADA data is unavailable, minimum daytime load can be estimated based on standard load profiles for various customer classes that many utilities maintain and update on an annual basis.

Figure 4 – This load profile indicates that minimum daytime load is significantly higher than absolute minimum load

Figure 5 - Relationship of peak load to minimum load for a large number of residential/commercial feeders in a southwest US city

## Apply Supplementary Screens

Applying supplementary screens to identify possible technical issues, regardless of penetration level, focuses on utilizing more comprehensive analyses as part of the initial review in order to eliminate the possibility of voltage regulation issues and the creation of unintentional islands. An example of this concept is shown in Figure 6.

Figure 6 – Modified SGIP screens to address PV interconnections regardless of penetration level

It is important that the additional screens are effective and relatively easy to apply. For example, Hawaii’s revised Rule 14H has clear timelines for when an application must be deemed complete, examined through initial review, and processed through supplemental review. Further, the California Rule 21 Supplemental Review Guideline contains several simple procedures that can be incorporated into the initial review screen for PV systems. With respect to voltage regulation, a procedure similar to Figure 7 is recommended for consideration. Note that the 15% in this drawing refers to the peak export on the line section, which is different than the SGIP 15% screen. The 15% peak export implies an instantaneous penetration level greater than 100%.

Figure 7 – Possible additional screening procedure for PV systems addressing voltage issues

Similarly for anti-islanding, Rule 21 Supplemental Review Guide contains a simple screen that can be applied as part of the initial review as seen in Figure 8. Application of the screen is more involved, but could be reasonably carried out as part of the Initial review since with only minimal amount of information required.

Figure 8 – Possible supplemental screening procedure for PV systems addressing unintentional islanding issues

## Utility Identified Zones of Penetration Levels

One concept for increasing penetration criteria is to identify zones where higher penetration is acceptable. These zones would be identified by utilities and would likely be located in areas closer to substations or with low-impedance conductors, thus having a lower potential for voltage abnormalities or protective system miscoordination. Figure 9  is an example area displaying zones that allow for greater penetration and those that require further study. These zones would change over time as new installations of DG come online. The California Energy Commission recently published a report that proposes several criteria for identifying project areas requiring minimal detailed studies. The report discusses a modeled system in which a wholesale PV project might have acceptable impact if connected in one location in a circuit, but may have significant impacts requiring mitigation or upgrades if connected in another location.

Figure 9 – An example area with zoned penetration limits

# Mid-Term and Long-Term Solutions

While short-term solutions may be applied in a one-year or less time frame, there are more promising solutions to be considered that will take years to develop and deploy. Mid-term solutions, for this paper, might be those that happen in the one to five year range, while long-term solutions are likely those beyond the five-year horizon.

## Upgrade Distribution Circuit Design for PV-Hosting Applications

Upgrading existing distribution feeders with larger-sized (thus lower impedance) conductors, installing voltage regulation devices, and increasing operating voltages (e.g. from 4kV to 13.2kV), are ways to maintain acceptable voltage levels and increase the PV hosting capacity of a feeder. Larger conductors and higher operating voltages allow greater levels of power delivery to loads as well as maintaining voltage levels, but there are financial impacts associated with these approaches.

New circuits designed and built in areas where there is anticipated PV development should be evaluated for increased conductor size and installation of voltage regulators. Existing distribution circuits can also be upgraded, but the process is often complicated and expensive. The cost of such upgrades would likely be shared between utilities and PV developers, but that policy issue is not discussed in detail in this paper.

Capital expenditures by utilities are constrained by the availability of financial resources and limited by regulatory agencies and financial organizations. If greater expenditures are encouraged, then regulated utilities will need approval from utility commissions and by the organizations that have financial oversight over the utilities. Investor-owned utilities have specific revenue to capital investment requirements necessary to maintain stock ratings, and this could be a significant issue when considering upgrading distribution circuits. Investor-owned utilities often issue stock to raise money for capital expenditure programs that include new and rebuilt distribution circuits. Other types of utilities, such as cooperatives and municipal-owned utilities have other difficulties in paying for upgrades.

## Develop Higher Accuracy Screening Metrics and Formulas

PV penetration metrics alone are insufficient indicators of the expected distribution system level impacts from PV interconnection. One potential solution is to develop more accurate screening metrics that can be used in a revised screening process. An interconnection impact metric for each PV interconnection concern, e.g. voltage effects, unintentional islanding, and protection coordination, could be developed. These metrics are functions of multiple distribution and PV system characteristics. For example, from previous high-penetration PV integration case studies, it is well known that a PV system’s nameplate capacity and distance from the distribution substation are key indicators of the expected voltage impacts of the PV system interconnection. A more reliable voltage impact metric can be formulated through extensive distribution system modeling using verified models that incorporate both the PV system nameplate capacity and the location of the interconnection on the distribution system. Other circuit characteristics and parameters, such as circuit voltage, conductor sizing, voltage regulation scheme, and the required service voltage range can also be considered in the development of a more reliable PV voltage impact metric. A sensitivity analysis for each considered circuit characteristic would then be performed and only the characteristics that largely determine the system impacts due to PV interconnection would be included in the final PV impact metric in order to simplify the calculation of the metric as much as possible.

The proposed PV impact metrics are more difficult to calculate than the current penetration metric (15%) but are still calculated based on available distribution circuit and PV system parameters. The developed PV impact metrics is a set of formulas that indicate whether the impacts of an individual PV interconnection exceed a given range agreed by the utilities and regulators similar to the PV penetration metric currently under use. Since PV impact metrics are developed for each interconnection concern and each metric takes into account a number of system characteristics and parameters, the resulting PV interconnection screening process allows more safe and compatible PV system to be interconnected without a supplemental interconnection study.

## Deploy Inverters with Advanced Functions

Today, the challenge involves integrating PV into the existing electrical distribution systems that were not designed for significant reverse power. Inverter grid support functions are either generally unavailable or unused. In the future, we expect investments and application of new technologies that will increase PV hosting capability. Although it will take time to implement, a new generation of inverters will be available with advanced functions designed to interact and support the grid.  Enabling these functions will involve setting up, preprogramming, reacting to grid condition signals, and implementing two-way communications with distribution operators. Also evolving is a smart grid with more automated distribution equipment and the ability to process information fed into both a central distribution management system and dispersed management systems that will manage accordingly. Advanced communication and control will enable the future distribution systems to better coordinate settings and limits of switch, protection, and voltage control devices as conditions change. Together, advanced inverter functions and more distribution automation are expected to significantly increase the PV hosting capability of the existing infrastructure.

Relative to other devices connected to utility distribution systems, PV inverters are highly capable in terms of responsiveness, controllability, processing capability, and memory Advanced inverters and controllers will provide real-time reactive power compensation, real power curtailment, watt-voltage, and watt-frequency management. Configurable autonomous actions can support the grid during abnormal voltage or frequency conditions. Previous studies have shown that advanced inverters can mitigate voltage-related issues and potentially increase the hosting capacity of solar PV by as much as 100%. This point is further illustrated in Figure 10, where the feeder voltage response is shown to improve with the use of advanced volt-VAr control.

Figure 10 – Feeder voltage response with advanced VAr control

Other functions, such as voltage and frequency ride-through, short-term or dynamic AC voltage support, inverter response to active anti-islanding, and arc-fault detection and mitigation, can increase reliability and safety.  Some smart grid functional modes that have been defined in a U.S. Department of Energy (DOE), Electric Power Research Institutes (EPRI), and Solar Electric Power Association (SEPA) collaboration are:

- Reactive Power/Power Factor Control Mode provides reactive power to the utility grid for spinning reserve scheduling or scheduled reactive power management.

- AC Voltage Control Mode provides dynamic AC line voltage regulation to increase the distribution line voltage stability and all coordination with utility distribution line equipment.

- Apparent Power Control Mode provides both real and reactive power whenever PV array power is less than the inverter power rating and minimizing operation of transformer tap or capacitor bank.

- Short Term Voltage Support reduces voltage fluctuations caused by sudden load changes on the distribution line by boosting short term reactive power within inverter thermal limit.

- Real Power Curtailment is employed in conjunction with other reactive power control modes reserving inverter output capacity for reactive power or to limit a plant’s maximum power output.

- Abnormal Voltage Ride Through supports the distribution grid when a power system fault occurs by providing both real and reactive power, rather than dropping of the grid.

- Coordinated Operation with Energy Storage mitigates adverse impacts on the grid due to the intermittent nature of the PV power source.

Taking advantage of advanced inverter functions, along with other opportunities for demand management, will require communication and control and, consequently, opportunities will evolve with a smarter distribution system. For PV inverters there will be potential to perform a large number of grid-supportive functions. The value of this functionality depends on the degree in which a grid operator can integrate PV functions with other distribution equipment. Some specific concepts are:

- Inverter VAR Generation in Coordination with Capacitor Banks. VAr management on distribution systems, when available, is typically provided by fixed or switched capacitors. Smart inverters, on the other hand, can provide variable VAr levels, both capacitive and inductive, but Watt losses may be higher. Methods by which the VAr capabilities of inverters are managed in coordination with capacitors in order to take advantage of the best characteristics of both need to be developed.

- Inverter Voltage Management in Coordination with Voltage Regulators. Voltage management on distribution systems is traditionally provided by load-tap-changing (LTC) transformers and line regulators. These devices adjust voltage within a specific range, but are limited in the number of adjustments that occur in a given timeframe due to physical limitations of the devices. The advanced inverter functionality will need to be capable of monitoring the local voltage levels and instantly modify both real and reactive power in response to voltage variations. Methods by which voltage management of inverters is incorporated into an integrated distribution voltage management scheme will need to be developed.

- Voltage Profile Shaping to Support Conservation Voltage Reduction. Conservation voltage reduction (CVR) is a method to reduce losses and end-use power consumption by holding voltage on a distribution system at a low level. The ability to implement CVR successfully is dependent on the voltage profile on the feeder.  Advanced inverter voltage functions demonstrated in several different field environments will be needed to show the potential for flattening of voltage profiles for CVR.

- Inverter Configuration in Coordination with Circuit Reconfiguration. As distribution systems become increasingly sectionalized and interconnected, switches can be used to isolate faults, minimize the scope of outages, and optimize efficiency.  Therefore a given PV system may be close to the substation in certain configurations and near the end of the feeder in others, necessitating different behaviors in order to be grid supportive.

In order to realize the capabilities of these advanced inverters, communication and control systems are needed. The connection will enable utility operators to interact from a central DMS to the PV plants as depicted in Figure 11.

Figure 11 – Critical elements to enable communications with distributed PV and storage

The acronyms used in Figure 11 are described as follows:

- GIS – geographic or geospatial information system

- CIS – customer information system

- OMS – outage management system

- CIM – common information model

- MDMS – meter data management system

- DMS – distribution management system

- SCADA – Supervisory Control and Data Acquisition

- CPV ( concentrating photovoltaic

- DNP – distributed network protocol

# Conclusions and Next Steps

Thousands of applications are submitted in the United States each year for PV installations and many states have aggressive renewable portfolio standards that encourage these installations. Therefore, it is critical that interconnection procedures be as streamlined as possible to avoid unnecessary interconnection studies, costs, and delays. There is an implicit expectation that existing interconnection procedures will evolve over time to reflect changes in standards, technology, and practical experience. Modifications to interconnection screens and procedures must have a focus on maintaining or improving safety and reliability, as well as reducing costs and improving expediency of the interconnection process.

Three short-term approaches have been presented for consideration. The first approach suggests utilizing PV-specific screening criteria that would utilize minimum daytime load for a circuit rather than absolute minimum load or a percentage of peak load. The second approach is to apply additional screens to evaluate potential voltage or unintentional island problems, regardless of penetration levels. The third approach would increase penetration levels in specific areas or zones based on substation location, circuit design, and existing DG. These three conceptual approaches may be considered as solution frameworks for increasing levels of PV deployment.

Mid-term and long-term solutions require close cooperation between regulatory agencies, electric utilities, national laboratories, DOE, EPRI, PV manufacturers, and developers. These solutions ultimately produce straightforward approaches to understand how much PV can be deployed on a circuit, and at what locations. Modeling, observation, testing, failure analysis, success analysis, and technology development is attainable through mutual cooperation and a focus on success.

# Footnotes

This is considered a rule of thumb for electric distribution engineers and is based on observation that the minimum load is, on average, approximately 30% of the peak annual load.

S. Gonzalez, M. R, A. Fresquez, M. Montoya, and N. Opell, "Multi-Inverter Utility Interconnection Evaluations", Proc, 37th IEEE PVSC, 2010.

A “stiff” location on a feeder would typically have a lower than average impedance and larger conductor capable of serving many megawatts of power to utility customers

Keller, J., Kroposki, B. (2010). Understanding Fault Characteristics of Inverter-Based Distributed Energy Resources. NREL Report No. TP-550-46698.

M. Braun et al. “Is the Grid Ready to Accept Large Scale PV Deployment? - State of the Art, Progress and Future Prospects”, Submitted to Progress in PV, to be published in 2012

See http://www.sce.com/AboutSCE/Regulatory/loadprofiles/2011loadprofiles.htm

http://www.energy.ca.gov/distgen/interconnection/model_rule.html

http://www.energy.ca.gov/2011publications/CEC-200-2011-014/CEC-200-2011-014.pdf

Braun, M., Stetz, T., Bründlinger, R., Mayr, C., Ogimoto, K., Hatta, H., Kobayashi, H., Kroposki, B., Mather, B., Coddington, M., Lynn, K., Graditi, G., Woyte, A. and MacGill, I. (2011), Is the distribution grid ready to accept large-scale photovoltaic deployment? State of the art, progress, and future prospects. Progress in Photovoltaics: Research and Applications. doi: 10.1002/pip.1204

Smith, J., Sunderman, W. Dugan, R., Seal, B., “Smart Inverter Volt/VAr Control Functions for High Penetration of PV on Distribution Systems”, 2011 Power Systems Conference and Exposition, Phoenix, Arizona, March 2011

# Text boxes

1/3/2012

+5%

+5%

-5%

-5%

Annual Daytime Minimum load was 1.8 MW at 9am, 32% of annual peak load

Annual Peak Load was 5.6 MW at 5pm

Annual Minimum load was 1.3 MW at 5am, 23% of annual peak load